## Slide 1: StreamDevice Introduction
Dirk Zimoch :: Paul Scherrer Institut
EPICS Collaboration Meeting October 2020 Fritz-Haber-Institut

## Slide 2: What is StreamDevice?
One generic EPICS driver for many different devices

## Slide 3: How can a Device Driver be Generic?
Separate similarities from differences
What do many devices have in common?
Command strings
Human readable Text
Fixed size (binary) “telegrams”
Limited set of buses
Serial (RS232, RS485, USB)
GPIB
Ethernet (TCP, UDP)
What is different between those devices?
Command sets
Command words
Terminators
Value encoding
Formatting
Position in the command
Configuration
Programming

## Slide 4: StreamDevice Architecture
StreamDevice
waveform
...
serial
TCP
GPIB
asynDriver
…
stringout
bo
ai
%f
%b
%{…}
%<…>
%/…/
Modular design allows to plug in new functionality
This is already done.
This is already done.
Record database (templates)
Protocol file
Startup script
This is what you have to do.

## Slide 5: StreamDevice and asynDriver
Is StreamDevice a replacement for asynDriver?
  No. In fact it uses asynDriver to talk to the hardware.
  To be exact: It uses the asynOctet interface.
But doesn’t asynDriver already come with device support?
  Yes, but for string based devices only stringin, stringout and char waveform.
StreamDevice does the string formatting and parsing and asynDriver does the hardware access.
Example:
ao VAL=3.1415
StreamDevice
Fetch value
3.1415 (double)
"SET %.2f\r\n"
Write output
"SET 3.14\r\n" (string)
asynDriver
RS232

## Slide 6: Example: Read a Device in 3 Easy Steps
Read Kelvin temperature #1 from a LakeShore 218 via RS232
  Command: “KRDG? 1” CR LF
  Reply: “+273.15” CR LF
Configure asynDriver port in startup script
      drvAsynSerialPortConfigure "LakeShore1","/dev/ttyS0“
      asynSetOption "LakeShore1", 0, "baud", "9600“
      asynSetOption "LakeShore1", 0, …
Write a protocol file, e.g. file LS218.prot
      Terminator = CR LF; temp_K_1 { out "KRDG? 1"; in "%f"; }
Write a record connecting to protocol file, protocol, and bus
      record (ai, "$(DEVICE):TEMP1") {
      field (DTYP, "stream") field (INP, "@LS218.prot temp_K_1 LakeShore1") field (EGU, "K")
      field (PREC, "2") }
File name and extension does not matter but I recommend to name it after the device type.
Protocol files are searched in ${STREAM_PROTOCOL_PATH}.

## Slide 7: Protocol Files
Have one file for each device type
  Best name it after device type
Set some global configuration of communication properties
Write one protocol for each function/command of device
Use out and in commands send and receive strings
Format/parse values with format converters like %f.
  Format converters work on implicit variables, typically VAL or RVAL fields.
  You can redirect to other fields or even other records
See: https://paulscherrerinstitute.github.io/StreamDevice/protocol.html
#LakeShore 218
Terminator = CR LF; ReplyTimeout = 1000; #ms ReadTimeout = 100; #ms
reset { out "*RST"; #no reply wait 2000; }
# read in Kelvin temp_K_1 { out "KRDG? 1"; in "%f"; }
# read in Celsius temp_C_1 { out "CRDG? 1"; in "%f"; }
Configuration variables
Protocol needs unique name within file
Comment: # until end of line
write constant string
read and parse reply string
if used by an ai record %f sets .VAL

## Slide 8: Strings in StreamDevice
Strings can be single or double quoted.
  "That's a string"
  'This one too'
Strings can be written in chunks, with or without comma
  "This is", ' one' " big" ' string'
Non-printable characters can be written in many ways: hex, oct, or dec number, escape sequence, symbolic name
  0x0a 012 10 "\x0a" "\012" "\10" "\n" LF NL
  0x00 0 "\x00" "\0" NUL
Alternatives can be freely mixed
  0x1b "00", 'PR3' CR
See: https://paulscherrerinstitute.github.io/StreamDevice/protocol.html#str
This is the way to break long strings into multiple lines.
For a list of symbolic names and escape sequences see the documentation.
Only difference: no need to escape the other quote type

## Slide 9: Formats as Known From printf/scanf
Standard formats
  %f, %e, %E, %g, %G, %d, %i, %x, %o, %s, %c, %[…]
  standard flags %0 -+# to modify format and %* to skip input
  new flags %? for optional input and %= for input comparison
  but no type modifiers like %hi or %lf
Additional formats and features
  %b (bit strings like "10010001")
  %r (raw machine format numbers)
  %{…|…|…} (enumerations)
  %<…> (checksums)
  %/…/ (regular expressions)
Variable is implicit, usually VAL or RVAL field
  Depends on converter type and record type
  Can be redirected like %(EGU)s or %(record)f
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html
These are just some examples.
More formats can be added.
"redirection" is explained later

## Slide 10: Enum Format: %{…|…|…}
Translates integers to enumerated strings and back
Example: Device can be switched with "STOP" and "GO" and can run forward or backward with different speeds (e.g. 1 or 5 mm/s) and reports this as "<<", "<", "=", ">", or ">>".
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html#enum
switch { out "%{STOP|GO}"; }
speed { out "DIR?"; in "DIR=%#{<<=-5|<=-1|\=|>>=5|>=1}" }
record(bo,"$(DEV):SWITCH") {
field(DTYP,"stream") field(OUT, "@$(PROTO) switch $(PORT)") field(ZNAM,"off") field(ONAM,"on") }
record(longin,"$(DEV):SPEED") {
field(DTYP,"stream")
field(INP, "@$(PROTO) speed $(PORT)") field(EGU, "mm/s")
}
0 = "STOP" 1 = "GO"
%#{ allows assignments: "<<" = -5 "<" = -1 "=" = 0 ">" = 1 ">>" = 5
Escape any literal | or } or = or \ in enum strings as \| or \} or \= or \\
>> before > to avoid wrong match
Input not matching any string raises INVALID/CALC alarm

## Slide 11: Checksums: %<…>
Many types of checksums supported
  sum, xor, crc (8,16,32 bit), adler32, …
Output: checksum is appended to output
Input: checksum is compared with input
Range selection: %<start>.<end><checksum>
  <start>: number of bytes to skip from beginning of string (default 0)
  <end>: number of bytes to skip just before %<…> (default 0)
Example: out "Example string%3.2<xor>";
Flag %0<…> switches to (upper case) hex digits instead of raw bytes
Flag %#<…> switches to little endian for multi-byte checksums
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html#chksum
Checksum mismatch raises INVALID/CALC alarm

## Slide 12: Binary Protocols (aka “Telegrams”)
Example: Send/receive 5 byte telegrams:
  Address, command, 2 byte value (little endian), xor-checksum
  Confirmation is the same with bit 8 set in command byte
Use %r to send/receive integers in "raw" machine code format
set_value { MaxInput = 5; out $1 0x04 "%#.2r%<xor>"; in $1 0x84 "%=#.2r%<xor>"; }
get_value { MaxInput = 5; out $1 0x44 0x00 0x00 "%<xor>"; in $1 0xc4 "%2r%<xor>"; }
pass address as parameter 1 (no \ outside quotes)
%= checks reply value
Add checksum
Test checksum
local configurations per protocol (overwrite globals)
Protocol does not use Terminators but has fixed size messages.

## Slide 13: Raw Format: %r and %R
Output format: %<flag><width>.<precision>r
  <flag> #: little endian (default is big endian)
  <width>: number of bytes printed (sign extended, default 1)
  <precision>: number of bytes taken from variable (default 1)
Example: value = 0xdeadbeef
  out "%2r"; 0xff 0xef 1 byte sign extended to 2 bytes
  out "%.2r"; 0xbe 0xef 2 bytes
  out "%#.4r"; 0xef 0xbe 0xad 0xde 4 bytes little endian
  out "%#4.2r"; 0xef 0xbe 0xff 0xff 2 bytes little endian sign extended to 4 bytes
Input format: %<flag><width>r
  <flag> #: little endian
  <flag> 0: zero extend to long (default is sign extend)
  <width>: number of bytes to read
%4R is float and %8R is double
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html#raw
Pitfall !
sorry for the mess out "%.2r" versus in "%2r"

## Slide 14: Regular expressions: %/…/and %#/…/…/
Uses Perl Compatible Regular Expressions (PCRE)
Normal regex: %/expression/ returns a string
  E.g. find keyword in long text: in "%.1/(?im)<title>(.*?)<\/title>/";
Regsub: %#/expression/substitution/ modifies input/output
  Make strange input readable:
    1.23-  -1.23 in "%#/([^+-])*([+-])/\2\1/%f";
    865+3  8.65e+3 in "%#/([0-9])([0-9]*)([-+][0-9]+)/\1.\2e\3/%f";
  Convert output to upper or lower case (and similar things)
    \path\x\y  /path/x/y out "%s%/\\/\//";
    Lower case hex checksum out "%s%0<xor>%#-2/.*/\L&/";
See: https://paulscherrerinstitute.github.io/StreamDevice/formats.html#regex
Get 1st sub expression here: (.*?)
Escape the /
Case insensitive multi-line match
%/…/ skips all input before match if expression does not start with ^
Last 2 bytes to lower case

## Slide 15: Protocol Parameters
Passing parameters from record to protocol can save typing.
Example: LakeShore218 has 8 temperatures
Terminator = CR LF; temp_K_1 {out "KRDG? 1"; in "%f";} temp_K_2 {out "KRDG? 2"; in "%f";} temp_K_3 {out "KRDG? 3"; in "%f";} temp_K_4 {out "KRDG? 4"; in "%f";} temp_K_5 {out "KRDG? 5"; in "%f";} temp_K_6 {out "KRDG? 6"; in "%f";} temp_K_7 {out "KRDG? 7"; in "%f";} temp_K_8 {out "KRDG? 8"; in "%f";}
Terminator = CR LF; temp_K {out "KRDG? \$1"; in "%f";}
record(ai,"$(DEVICE):TEMP2") {
field(DTYP,"stream") field(INP,"@LS218.prot temp_K(2) $(PORT)") field(EGU,"K") field(PREC,"2") }
Use parameter instead: "\$1" is 1st parameter.
Pass value for 1st parameter.
Up to 9 parameters possible.
record(ai,"$(DEVICE):TEMP2") {
field(DTYP,"stream") field(INP,"@LS218.prot temp_K_2 $(PORT)") field(EGU,"K") field(PREC,"2") }

## Slide 16: Redirections
Normally format converters choose field automatically
  VAL or RVAL, depending on format data type
  Scaling (ASLO, AOFF) and smoothing (SMOO) are supported
But sometimes other fields or even other records are needed
  e.g. when one message contains more than one value.
Examples:
  Write value and units: out "%f %(EGU)s";
  Read status and value: in "%(otherrecord.FIELD)d,%f";
Other records must be on the same IOC.
Use parameters to avoid record names in protocols.
  Like "%(\$1)d" or "%(\$1:STATUS)d"
If no field is given .VAL is assumed.
Pass full record name as parameter.
Pass only part of record name as parameter.

## Slide 17: Redirection Example
Example: "position?" request gives reply with 6 coordinates. "position( 1.2 , 2.1234, 23.12 ,-2.312 ,-12.33 ,24.4321)"
pos { out "position?"; in "position(%f\_," "%(\$1:POS-Y)f\_," "%(\$1:POS-Z)f\_," "%(\$1:POS-RX)f\_," "%(\$1:POS-RY)f\_," "%(\$1:POS-RZ)f\_)"; }
record(ai,"$(DEV):POS-X") {
field(DTYP,"stream") field(INP, "@$(PROT) pos($(DEV)) $(PORT)") field(EGU, "mm") field(PREC,"2") field(SCAN,"5 second")
field(FLNK,"…")
}
record(ai,$(DEV):POS-Y) {
field(EGU, "mm")
field(PREC,"2")
}
…
record(ai,$(DEV):POS-RZ) {
field(EGU, "deg")
field(PREC,"3")
}
When FLNK is processed, the other records have already got their values.
These records have SCAN="Passive" and DTYP="Soft Channel"
When redirecting to .RVAL use
DTYP="Raw Soft Channel"
Redirection to other records uses dbPutField() and thus processes the target if the field (here .VAL) is PP
Spaces around numbers:
%f accepts leading whitespace. Any amount of trailing whitespace is consumed by \_.

## Slide 18: Complex Protocol: Pfeiffer MaxiGauge
Send device address (on RS485) ESC (=0x1b) "aa"
  aa is address 00, 01, …
Send pressure read command: "PRn" CR n is sensor number 1 … 6
Each command is acknowledged with ACK (=0x06) CR LF
After acknowledge request value with ENQ (=0x05)
Receive status and pressure: "0,1.234E-5" CR LF
InTerminator = CR LF; # no OutTerminator because of ENQ pressure { out ESC "0\$1" "PR\$2" CR; in ACK; out ENQ; in "%(\$3:STATUS)d,%f"; }
sensor
record(ai,"$(D):PRESSURE") {
field(DTYP,"stream") field(INP, "@%(PROT) pressure($(A),$(S),$(D)) $(B)") }
record(mbbi,"$(D):STATUS") { field(ZRST,"OK") field(ONST,"Underrange") field(TWST,"Overrange")
… }
Pass address, sensor and device name as 3 parameters.
address
Redirect status to other record.
Keep pressure in active record.

## Slide 19: Arrays
For arrays the format is repeated for each element with optional separator string in between.
Example: "VALUE=[10.2,345.3,23.3,10.0]"
Input
  reads a maximum of NELM elements
  at least one element must be found
  sets NORD to number of elements found
Output
  writes NORD elements
readArray { Separator = ","; in "VALUE=[%f]"; }
record(aai,"$(DEVICE):Array") {
field(FTVL,"FLOAT")
field(NELM,"100") field(DTYP,"stream")
field(INP, "@$(PROT) readArray $(PORT)") }
Tables don’t work!
1.234 4.233 3.424 2.321 6.342 3.121
1.122 5.324 2.134
↓ ↓ ↓
record A record B record C

## Slide 20: Asynchronous input: I/O Intr
Some devices send unsolicited data
Example: Temperature sensor sends periodically: "+27.3 C" CR LF
Asynchronous records have SCAN="I/O Intr".
Asynchronous protocols typically have only an in command.
Any input from that device is checked.
  Including input going to other protocols
  Record is processed whenever matching input is found.
  Non-matching input is silently ignored (no error).
Terminator = CR LF;
temperature { in "%f C"; }
record(ai,"$(DEVICE):TEMP") {
field(DTYP,"stream") field(INP, "@$(PROT) temperature $(PORT)") field(EGU, "C") field(PREC,"1")
field(SCAN,"I/O Intr") }

## Slide 21: I/O Intr vs. Redirection
Example: Read input line with two values x and y every second
x { out "xy?"; in "%f %*f"; }
y { in "%*f %f"; }
record(ai,"$(D):x") {
field(SCAN,"1 second") field(DTYP,"stream") field(INP, "@$(PROT) x $(PORT)") }
record(ai,"$(D):y") {
field(SCAN,"I/O Intr") field(DTYP,"stream")
field(INP, "@$(PROT) y $(PORT)")
}
Ignore second value.
Ignore first value.
Be careful:
Any input with two numbers matches.
x { out "xy?"; in "%f %(\$1:y)f"; }
record(ai,"$(D):x") {
field(SCAN,"1 second") field(DTYP,"stream") field(INP, "@$(PROT) x($(D)) $(PORT)") }
record(ai,"$(D):y") {
field(SCAN,"Passive") field(DTYP,"Soft Channel")
}
y is processed when x writes value to it.
Redirect second value.
Redirection is more selective.
Only input from x goes to y.
y is processed when anyone receives input that matches.

## Slide 22: Error Handling
All errors set SEVR to INVALID.
  STAT depends on error type:
    Reply timeout: Device does not reply.  TIMEOUT
    Read timeout: Device stops sending unexpectedly.  READ
    Write timeout: Writing failed.  WRITE
    Lock timeout: Bus is blocked by other records.  TIMEOUT
    Mismatch: Input does not match format string.  CALC
Errors abort the protocol
  but may trigger exception handlers .
Errors are not propagated along redirections.
  Redirections before mismatch are processed normally.
  Redirections after mismatch are not processed at all.
  Only active record gets error status.
Mismatch in "I/O Intr" records is silently ignored.
I am planning to change that.

## Slide 23: Exception Handlers
Jump to different protocol if something goes wrong
  @mismatch, @replyTimeout, @readTimeout, @writeTimeout
Example: Device replies with value or error message
readValue { out "value?"; in "%f"; @mismatch { in "%(\$1:ErrorString)39c"; } }
If input does not match "%f" jump to @mismatch.
Reparse input and redirect.
record(ai,"$(DEVICE):Value") {
field(DTYP,"stream") field(INP, "@$(PROT) readValue($(DEVICE)) $(PORT)") }
record(stringin,"$(DEVICE):ErrorString") { }
Exception handlers can be defined before or inside normal protocol.
If input does not match and the @mismatch handler starts with in, then the same input is parsed a second time.

## Slide 24: Record Initialization
Output records can be initialized from hardware
  Initialization is formally handled as an exception: @init
getVolt { out "VOLT?"; in "VOLT %f"; }
setVolt { out "VOLT %.2f"; @init {getVolt;} }
getFreq { out "FREQ?"; in "FREQ %f MHZ"; }
setFreq { out "FREQ %.6f MHZ"; @init {getFreq;} }
@init is executed in iocInit before scans are started, when ioc is un-paused and when device re-connects.
record(ai,"$(D):ReadVoltage") {
field(DTYP,"stream") field(INP, "@$(PROT) getVolt $(PORT)") } record(ao,$(D):SetVoltage") { field(DTYP,"stream") field(OUT, "@$(PROT) setVolt $(PORT)") }
record(ai,"$(D):ReadFrequency") {
field(DTYP,"stream") field(INP, "@$(PROT) getFreq $(PORT)") }
record(ao,$(D):SetFrequency") { field(DTYP,"stream") field(OUT, "@$(PROT) setFreq $(PORT)") }
Reference other protocol to insert all its commands.

## Slide 25: Recommended Reading
StreamDevice documentation
    https://paulscherrerinstitute.github.io/StreamDevice
AsynDriver documentation:
    https://epics-modules.github.io/master/asyn
Record Reference Manual
    https://wiki-ext.aps.anl.gov/epics/index.php/RRM_3-14 https://epics.anl.gov/base/R3-15/8-docs/RecordReference.html
    https://epics.anl.gov/base/R7-0/4-docs/RecordReference.html
EPICS How-To pages "Getting started"
  https://docs.epics-controls.org/projects/how-tos
Perl Compatible Regular Expressions (PCRE)
  https://www.pcre.org/current/doc/html/pcre2syntax.html